## Sheet1
Test Cases
Not Tested
Passed
Failed
| NA | 0
| Total Tests | 0
Sr.no | Functionality | Test Case ID | Test Type | Test Case Objective | Test Steps | Precondition | Test Scenario Type | Test Data | Expected Results | Actual Results | Build | Dated | Result | Defect Id | Test log | Remarks
1 | Read Property Service Initiation Test | TC_RP_01 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read a Property- List property and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from the Objects tab Property :- Property List 371 | 1. After step 4, Explorer should initiate RP request for specified Object with Property- List property. 2. After step5, Explorer should display the value received in response. | The Property List property of all Objects initiates an RP request and is present in the IUT database; however, the Property List property of all Objects is not visible on the Explorer. | 1.07.06-82 | 2025-02-05
2 | Read Property Service Initiation Test | TC_RP_02 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Analog Input Object and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Review response from TD. | 1. Software should be initialized. | Positive | Refer test data for Analog Input Objects tab Properties :- All properties present in database | 1. After step 4, Explorer should initiate RP request for Analog Input Object with all properties 2. After step5, Explorer should display the value received in response. | Read Property service is not initiated through Explorer for any property of Analog Input Object except Property-List | 1.07.06-82 | 2025-02-05
3 | Read Property Service Initiation Support | TC_RP_03 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Analog Output and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Review response from TD. | 1. Software should be initialized. | Positive | Refer test data for Analog Output Objects tab Properties :- All properties present in database | 1. After step 4, Explorer should initiate RP request for Analog Output Object with all properties 2. After step5, Explorer should display the value received in response. | Read Property service is not initiated through Explorer for any property of Analog Output Object except Property-List | 1.07.06-82 | 2025-02-05
4 | Read Property Service Initiation Support | TC_RP_04 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Device Object and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data for Device Objects tab Properties :- All properties present in database | 1. After step 4, Explorer should initiate RP request for Device Object with all properties 2. After step5, Explorer should display the value received in response. | Read Property service is not initiated through Explorer for any property of Device Object except Property-List | 1.07.06-82 | 2025-02-05
5 | Read Property Service Initiation Support | TC_RP_05 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Analog Value and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from the Analog Value Objects tab Properties :- All properties present in database | 1. After step 4, Explorer should initiate RP request for Analog value Object with all properties 2. After step5, Explorer should display the value received in response. | Read Property service is not initiated through Explorer for any property of Analog Value except Property-List | 1.07.06-82 | 2025-02-05
6 | Read Property Service Initiation Support | TC_RP_06 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Binary Input and can correctly process the response | 1. Initialize Software. 2. Initiate Read Property service request from Software as mentioned in test data. 3. Verify the request initiated on Wireshark whether it has all the parameters as mentioned in test data. 4. Verify the response received on Wireshark. | 1. Software should be initialized. | Positive | Refer test data from the Binary Input Objects tab Properties :- All properties present in database | Read Property service request should be initiated successfully to read any property and can correctly process the response. | Read Property service is not initiated through Explorer for any property of Binary Input except Property-List | 1.07.06-82 | 2025-02-05
7 | Read Property Service Initiation Support | TC_RP_07 | Functional | To verify that, from Software, Read Property service request is initiated successfully to read any properties of an Binary-output and can correctly process the response. | 1. Initialize Software. 2. Initiate Read Property service request from Software as mentioned in test data. 3. Verify the request initiated on Wireshark whether it has all the parameters as mentioned in test data. 4. Verify the response received on Wireshark. | 1. Software should be initialized. | Positive | Refer test data from the Binary Output Objects tab Properties :- All properties present in database | Read Property service request should be initiated successfully to read any property and can correctly process the response. | Read Property service is not initiated through Explorer for any property of Binary Output | 1.07.06-82 | 2025-02-05
8 | Read Property Multiple Service Initiation Support | TC_RPM_01 | Functional | To verify that, from Software, Read Property Multiple service request is initiated successfully to read any properties of an Binary Output and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from Binary output Objects tab Properties :- All properties present in database | 1. After step 4, Explorer should initiate RPM request for Binary Output Object with any property. 2. After step5, Explorer should display the value received in response. | Read Property Multiple service is initiated through Explorer for any property of Binary Output | 1.07.06-82 | 2025-02-18
9 | Read Property Multiple Service Initiation Support | TC_RPM_02 | Functional | To verify that, from Software, Read Property Multiple service request is initiated successfully to read any properties of an Binary Input and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from Binary Objects input tab Properties :- All properties present in database | 1. After step 5, Explorer should initiate RPM request for Binary Input Object with any property. 2. After step5, Explorer should display the value received in response. | Read Property Multiple service is initiated through Explorer for any property of Binary Input | 1.07.06-82 | 2025-02-18
10 | Read Property Service Initiation Support | TC_RP_08 | Functional | To verify that, Software initiates Read Property service request with Array Index 0 | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from Objects tab Properties :- any properties | 1. After step 5, Explorer should initiate RP request for any property of specified object with Array index 1(Between 1 to 16) 2. After step 5, Explorer should display the value received in response. | Read Property service is initiated through Explorer for any Writable properties with array index 1(Between 1 to 16) |  | 2025-02-27
11 | Write Property Service Initiation Support | TC_WP_01 | Functional | To verify that, from Software, Write Property service request is initiated successfully to write an Array property with array index 0 and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg AO) 5. Double click on any property(eg Priority array) to write 6. Revise response from TD. | 1. Software should be initialized. | Positive | Refer test data from Objects tab Properties :- Array Property | 1. After step 5, Explorer should initiate WP request for any Array property of specified object(eg AO, Priority array) with Array index 0 2. After step5, Explorer should display the value received in response. | Write Property service is initiated through Explorer for Array Properties with Array index 0 |  | 2025-02-25
12 | Read Property Multiple Service Initiation Support | TC_RPM_03 | Functional | To verify that, from Software, Read Property Multiple service request is initiated successfully to read a complex property and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Double click on property to write 6. Revice response from TD. | 1. Software should be initialized. | Positive | Refer test data from the Objects tab | Read Property Multiple service request should be initiated successfully to read complex property and can correctly process the response. |  |  | 2025-02-25
13 | Read Property Multiple Service Initiation Support | TC_RPM_04 | Functional | To verify that, from Software, Read Property Multiple service request is initiated successfully to read BACnetPropertyAccessResult and BACnetARRAY[N] of BACnetPropertyAccessResult properties and can correctly process the response. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object to be tested. 5. Double click on property to write 6. Revice response from TD. | 1. Software should be initialized. | Positive |  | Read Property Multiple service request should be initiated successfully to read BACnetPropertyAccessResult and BACnetARRAY[N] of BACnetPropertyAccessResult properties and can correctly process the response.
14 | Segmentation Supported Property Validation | TC_SS_01 | Functional | To verify that, Web server initiates Read Property Multiple service request for the test device that supports Segmented_Both value of Segmentation_Supported property of device object. | 1. Initialize Software. 2. Select the test device having Segmented_Both value for the Segmentation_Supported property of device object. 3. Verify that Web server initializes Read Property Multiple service request on Wireshark. 4. Verify that TD responded with segments. 5. Verify that all the objects of TD are displayed on UI. | 1. Software should be initialized. 2. Max APDU Length Accepted property of device object should have value 128. | Positive |  | Stack should initiate Read Property Multiple service request for the test device that supports Segmented_Both value of Segmentation_Supported property of device object.
15 | Segmentation Supported Property Validation | TC_SS_02 | Functional | To verify that, Web server initiates Read Property Multiple service request for the test device that supports Segmented Transmit value of Segmentation_Supported property of device object. | 1. Initialize Software. 2. Select the test device having Segmented Transmit value for the Segmentation_Supported property of device object. 3. Verify that Web server initializes Read Property Multiple service request on Wireshark. 4. Verify that TD responded successfully. 5. Verify that all the objects of TD are displayed on UI. | 1. Software should be initialized. 2. Max APDU Length Accepted property of device object should have value 128. | Positive |  | Stack should initiate Read Property Multiple service request for the test device that supports Segmented Transmit value of Segmentation_Supported property of device object.
16 | Segmentation Supported Property Validation | TC_SS_03 | Functional | To verify that, Web server initiates Read Property Multiple service request for the test device that supports Segmented Receive value of Segmentation_Supported property of device object. | 1. Initialize Software. 2. Select the test device having Segmented Receive value for the Segmentation_Supported property of device object. 3. Verify that Web server initializes Read Property Multiple service request on Wireshark. 4. Verify that TD responded successfully. 5. Verify that all the objects of TD are displayed on UI. | 1. Software should be initialized. 2. Max APDU Length Accepted property of device object should have value 128. | Positive |  | Stack should initiate Read Property Multiple service request for the test device that supports Segmented Receive value of Segmentation_Supported property of device object.
17 | Segmentation Supported Property Validation | TC_SS_04 | Functional | To verify that, Web server initiates Read Property service request for the test device that supports No Segmentation value of Segmentation_Supported property of device object. | 1. Initialize Software. 2. Select the test device having No Segmentation value for the Segmentation_Supported property of device object. 3. Verify that Web server initializes Read Property Multiple service request on Wireshark. 4. Verify that TD responded with error as "Segmentation-Not-Supported". 5. Verify that web server initiates Read Property service request to read the data. 6. Verify that TD responded to received Read Property service requests. 7. Verify that all the objects of TD are displayed on UI. | 1. Software should be initialized. 2. Max APDU Length Accepted property of device object should have value 128. | Positive |  | Stack should initiate Read Property service request for the test device that supports No Segmentation value of Segmentation_Supported property of device object.
18 | Read Property Multiple Service Initiation Support | TC_WP_05 | Functional | To verify that, web server supports fallback mechanism when test device does not support WRITE Property Multiple service. | 1. Initialize Software. 2. Click on the TD which does not support Read Property Multiple service execution. 3. Verify that TD responded with error as "Unrecognized Service". 4. Verify that web server initiates Read Property service request to read all the data of TD. 5. Verify that TD responded to all the requests received. 6. Verify that, on Software, all the objects present in TD and properties of those objects are displayed. | 1. Software should be initialized. 2. Test Device should not support Read Property Multiple service request execution. | Positive |  | Web server should support fallback mechanism when test device does not support Read Property Multiple service.
19 | Array Property Validation Support | TC_AP_01 | Functional | To verify that, Software initiates Read Property and Write Property service request with Array Index 0 to read and write the Array Size. | q | 1. Software should be initialized. | Positive |  | Software should initiate Read Property and Write Property service request with Array Index 0 to read and write the Array Size.
20 | Array Property Validation Support | TC_AP_02 | Functional | To verify that, Software initiates Read Property and Write Property service request with valid Array Index to read and write an array element. | 1. Initialize Software. 2. Initiate Read Property service request from Software for the array properties mentioned in test data with any valid Array index. 3. Verify that the response is received on UI with the value of an array element. 4. Initiate Write Property service request from Software for the array properties mentioned in test data to write the array element using any valid Array index. 5. Verify that Write Property service request is initiated to write an array element. 6. Execute above steps with Read Property Multiple and Write Property Multiple services also. | 1. Software should be initialized. | Positive |  | Software should initiate Read Property and Write Property service request with valid Array Index to read and write an array element.
21 | Write Property Service Initiation Support | TC_WP_02 | Functional | To verify that, Software initiates Write Property service request | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Aanalog Input) 5. Double click on any property(eg Present Value) to write 6. Revice response from TD. | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Properties :- Any writable properties | 1. After step 5, Explorer should initiate WP request for any writable property of specified Object 2. After step5, Explorer should display the value received in response. | Write Property service is initiated through Explorer for any Writable properties | 1.07.06-82 | 2025-02-18
22 | Write Property Service Initiation Support | TC_WP_03 | Functional | To verify that, Software initiates Write Property service request with Array Index 0 | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg AI) 5. Double click on any property(eg Present value) to write 6. Revice response from TD. | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Properties :- any writable properties | 1. After step 5, Explorer should initiate WP request for any property of specified object with priority 1(Between 1 to 16) 2. After step5, Explorer should display the value received in response. | Write Property service is initiated through Explorer for any Writable property of specified object with priority 1(Between 1 to 16)
23 | Write Property Service Initiation Support | TC_WP_04 | Functional | To verify that, Software initiates Write Property service request with Array Index 0 | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg AI) 5. Double click on any property(eg Present value) to write 6. Revice response from TD. | 1. Software should be initialized. | Positive | Refer test data from Objects tab Properties :- any writable properties | 1. After step 5, Explorer should initiate WP request for any property of specified object with Array index 1(Between 1 to 16) 2. After step 5, Explorer should display the value received in response. | Write Property service is initiated through Explorer for any Writable properties with array index 1(Between 1 to 16)
24 | Write Property Service Initiation Support | TC_WP_04 | Functional | To verify that , Software should initiate WP request to write Object Name property of any object(eg Analog value, Analog input) with "0" length i.e. blank string | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Double click on Object Name property and write value (Blank string) 6. Enter after writing the value 7. Revice response from TD | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Object: Any Object Properties :- Object name Value: blank string (" ") | 1. After step 6, Explorer should initiate WP request to write Object name property with "0" value as blank string 2. After step6, Verify that the Explorer displays the values received in Wireshark log | Write Property service is initiated through Explorer to write object name property of any object(eg Analog value, Analoginput) with "0" length i.e. blank string | 1.07.06-82 | 2025-02-19
25 | Write Property Service Initiation Support | TC_WP_05 | Functional | To verify that, Software initiate WP to write Present Value property of Multistate Value with "0" | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Multistate Value) 5. Double click on Present Value to write value (Blank string) 6. Enter after writing the value 7. Revice response from TD | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Object: Multistate Value Properties :- Present Value Value : 0 | 1. After step 6, Explorer should initiate WP request to write present value with "0" of multistate value 2. After step6,Verify that the Explorer displays the values received in Wireshark log | Write Property service is initiated through Explorer write Present value property of Multistate Value with "0" | 1.07.06-82 | 2025-02-19
26 | Write Property Service Initiation Support | TC_WP_06 | Functional | To verify that, Software initiates WP to write Relinquish Default property of Multistate Value with "0" | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg MSV) 5. Double click on Relinquish Default property to write "0" 6. Enter after writing the value 7. Revice response from TD | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Object: Multistate Value Properties :- Relinquish Default Value : 0 | 1. After step 6, Explorer should initiate WP request to write Relinquish Default with "0" of Multistate Value 2. After step6,Verify that the Explorer displays the values received in Wireshark log | Write Property service is initiated through Explorer to write relinquish default property of Multistate value with "0" | 1.07.06-82 | 2025-02-19
27 | Read Property Multiple Service Initiation Support | TC_RPM_05 | Functional | To verify that, Software initiates RPM to read Object identifier property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Device) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: any Object Properties :- Object identifier | 1. After step 4, Explorer should initiate RPM request for Object identifier property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Object identifier property of any Object | 1.07.06-82 | 2025-02-20
28 | Read Property Multiple Service Initiation Support | TC_RPM_06 | Functional | To verify that, Software initiates RPM to read Object Name property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Device) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Object Name | 1. After step 4, Explorer should initiate RPM request for Object Name property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Object Name property of any Object | 1.07.06-82 | 2025-02-20
29 | Read Property Multiple Service Initiation Support | TC_RPM_07 | Functional | To verify that, Software initiates RPM to read Object Type property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Device) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Object Type | 1. After step 4, Explorer should initiate RPM request for Object Type property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Object Type property of any Object | 1.07.06-82 | 2025-02-20
30 | Read Property Multiple Service Initiation Support | TC_RPM_08 | Functional | To verify that, Software initiates RPM to read Present Value property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Present Value | 1. After step 4, Explorer should initiate RPM request for Present Value property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Present Value property of any Object | 1.07.06-82 | 2025-02-20
31 | Read Property Multiple Service Initiation Support | TC_RPM_09 | Functional | To verify that, Software initiates RPM to read Status Flag property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Status Flag | 1. After step 4, Explorer should initiate RPM request for Status Flag property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Status Flag property of any Object | 1.07.06-82 | 2025-02-21
32 | Read Property Multiple Service Initiation Support | TC_RPM_10 | Functional | To verify that, Software initiates RPM to read Out of Service property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Revice response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Out of Service | 1. After step 4, Explorer should initiate RPM request for Out of Service property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Out of Service of any Object | 1.07.06-82 | 2025-02-21
33 | Read Property Multiple Service Initiation Support | TC_RPM_11 | Functional | To verify that, Software initiates RPM to read Profile Name property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Profile Name | 1. After step 4, Explorer should initiate RPM request for Profile Name Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Profile Name of any Object | 1.07.06-82 | 2025-02-24
34 | Read Property Multiple Service Initiation Support | TC_RPM_12 | Functional | To verify that, Software initiates RPM to read Event State property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Event State | 1. After step 4, Explorer should initiate RPM request for Event State Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event State of any Object | 1.07.06-82 | 2025-02-24
35 | Read Property Multiple Service Initiation Support | TC_RPM_13 | Functional | To verify that, Software initiates RPM to read Reliability property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Reliability | 1. After step 4, Explorer should initiate RPM request for Reliability Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Reliability of any Object | 1.07.06-82 | 2025-02-25
36 | Read Property Multiple Service Initiation Support | TC_RPM_14 | Functional | To verify that, Software initiates RPM to read Local Date, Local Time property of Device Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Device Object Property :- Local Date, Local Time | 1. After step 4, Explorer should initiate RPM request for Local Date, Local Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Local Date, Local Time of Device Object | 1.07.06-82 | 2025-02-25
37 | Read Property Multiple Service Initiation Support | TC_RPM_15 | Functional | To verify that, Software initiates RPM to read Units property of any Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Any Object Property :- Units | 1. After step 4, Explorer should initiate RPM request for Units Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Units of any object | 1.07.06-82 | 2025-02-25
38 | Read Property Multiple Service Initiation Support | TC_RPM_16 | Functional | To verify that, Software initiates RPM to read Utc-Offset property of Device Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Device Object Property :- Utc-Offset | 1. After step 4, Explorer should initiate RPM request for Utc-Offset Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Utc-Offset property of Device Object | 1.07.06-82 | 2025-02-25
39 | Read Property Multiple Service Initiation Support | TC_RPM_17 | Functional | To verify that, Software initiates RPM to read Vendor Name property of Device Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Analog Input) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Device Object Property :- Vendor Name | 1. After step 4, Explorer should initiate RPM request for Vendor Name Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Name property of Device Object | 1.07.06-82 | 2025-02-25
40 | Write Property Service Initiation Support | TC_WP_07 | Functional | To verify that Software automatically triggers a Read Property request following every Write Property request. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg MSV) 5. Double click on any property (eg Object Name) 6. Enter after writing the value 7. Review response from TD | 1. Software should be initialized. 2. Writable properties should be present | Positive | Refer test data from Objects tab Object: Any Object Properties :- Any Property | 1. After step 5, Explorer should initiate WP request 2. After step6,Verify that the Explorer triggers Read property request following Write property request | Read Property service is not initiated through Explorer for every Write property request | 1.07.06-82 | 2025-02-25
41 | Read Property Multiple Service Initiation Support | TC_RPM_18 | Functional | To verify that, Software initiates RPM to read Daylight-Savings-Status property of Device Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Device Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Device Object Property :- Daylight-Savings-Status | 1. After step 4, Explorer should initiate RPM request for Daylight-Savings-Status Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Daylight-Savings-Status property of Device Object | 1.07.06-82 | 2025-02-26
42 | Read Property Multiple Service Initiation Support | TC_RPM_19 | Functional | To verify that, Software initiates RPM to read Apdu-Timeout property of Device Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Device Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Device Object Property :- Apdu-Timeout | 1. After step 4, Explorer should initiate RPM request for Apdu-Timeout Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Apdu-Timeout property of Device Object | 1.07.06-82 | 2025-02-26
43 | Read Property Multiple Service Initiation Support | TC_RPM_20 | Functional | To verify that, Software initiates RPM to read Notification-Class property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :- Notification-Class | 1. After step 4, Explorer should initiate RPM request for Notification-Class Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notification-Class property of Device Object | 1.07.06-82 | 2025-02-26
44 | Read Property Multiple Service Initiation Support | TC_RPM_21 | Functional | To verify that, Software initiates RPM to read Priority property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :- Priority | 1. After step 4, Explorer should initiate RPM request for Priority Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Priority property of Notification-Class Object | 1.07.06-82 | 2025-02-26
45 | Read Property Multiple Service Initiation Support | TC_RPM_22 | Functional | To verify that, Software initiates RPM to read Ack-Required property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :- Ack-Required | 1. After step 4, Explorer should initiate RPM request for Ack-Required Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Ack-Required property of Notification-Class Object | 1.07.06-82 | 2025-02-26
46 | Read Property Multiple Service Initiation Support | TC_RPM_23 | Functional | To verify that, Software initiates RPM to read Recipient-List property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Recipient-List | 1. After step 4, Explorer should initiate RPM request for Recipient-List Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Recipient-List property of Notification-Class Object | 1.07.06-82 | 2025-02-26
47 | Read Property Multiple Service Initiation Support | TC_RPM_24 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Notification-Class Object | 1.07.06-82 | 2025-02-26
48 | Read Property Multiple Service Initiation Support | TC_RPM_25 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Notification-Class Object | 1.07.06-82 | 2025-02-26
49 | Read Property Multiple Service Initiation Support | TC_RPM_26 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Notification-Class Object | 1.07.06-82 | 2025-02-26
50 | Read Property Multiple Service Initiation Support | TC_RPM_27 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Notification-Class Object | 1.07.06-82
51 | Read Property Multiple Service Initiation Support | TC_RPM_28 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Notification-Class Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Notification-Class Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification-Class Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Notification-Class Object | 1.07.06-82
52 | Read Property Multiple Service Initiation Support | TC_RPM_29 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg file Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of File Object | 1.07.06-82 | 2025-02-26
53 | Read Property Multiple Service Initiation Support | TC_RPM_30 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Schedule Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Schedule Object | 1.07.06-82 | 2025-02-26
54 | Read Property Multiple Service Initiation Support | TC_RPM_31 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BV Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Binary Value Object | 1.07.06-82 | 2025-02-26
55 | Read Property Multiple Service Initiation Support | TC_RPM_32 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Binary Value Object | 1.07.06-82 | 2025-02-26
56 | Read Property Multiple Service Initiation Support | TC_RPM_33 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Binary Input Object | 1.07.06-82 | 2025-02-26
57 | Read Property Multiple Service Initiation Support | TC_RPM_34 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Multistate Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg Multistate Value Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Multistate Value Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Multistate Value Object | 1.07.06-82 | 2025-02-27
58 | Read Property Multiple Service Initiation Support | TC_RPM_35 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Multistate Value Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Multistate Value Object | 1.07.06-82 | 2025-02-27
59 | Read Property Multiple Service Initiation Support | TC_RPM_36 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Analog Output Object | 1.07.06-82 | 2025-02-27
60 | Read Property Multiple Service Initiation Support | TC_RPM_37 | Functional | To verify that, Software initiates RPM to read Vendor Proprietary property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :-Vendor Proprietary | 1. After step 4, Explorer should initiate RPM request for Vendor Proprietary Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Vendor Proprietary property of Analog Input Object | 1.07.06-82 | 2025-02-27
61 | Read Property Multiple Service Initiation Support | TC_RPM_38 | Functional | To verify that, Software initiates RPM to read Min-Pres-Value property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :-Min-Pres-Value | 1. After step 4, Explorer should initiate RPM request for Min-Pres-Value Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Min-Pres-Value property of Analog Input Object | 1.07.06-82 | 2025-02-27
62 | Read Property Multiple Service Initiation Support | TC_RPM_39 | Functional | To verify that, Software initiates RPM to read Max-Pres-Value property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :-Max-Pres-Value | 1. After step 4, Explorer should initiate RPM request for Max-Pres-Value Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Max-Pres-Value property of Analog Input Object | 1.07.06-82 | 2025-02-27
63 | Read Property Multiple Service Initiation Support | TC_RPM_40 | Functional | To verify that, Software initiates RPM to read Cov-Increment property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :-Cov-Increment | 1. After step 4, Explorer should initiate RPM request for Cov-Increment Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Cov-Increment property of Analog Input Object | 1.07.06-82 | 2025-02-27
64 | Read Property Multiple Service Initiation Support | TC_RPM_41 | Functional | To verify that, Software initiates RPM to read Notification-Class property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :-Notification-Class | 1. After step 4, Explorer should initiate RPM request for Notification-Class Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notification-Class property of Analog Input Object | 1.07.06-82 | 2025-02-27
65 | Read Property Multiple Service Initiation Support | TC_RPM_42 | Functional | To verify that, Software initiates RPM to read High Limit property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- High Limit | 1. After step 4, Explorer should initiate RPM request for High Limit Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read High Limit property of Analog Input Object | 1.07.06-82 | 2025-02-27
66 | Read Property Multiple Service Initiation Support | TC_RPM_43 | Functional | To verify that, Software initiates RPM to read Low Limit property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Low Limit | 1. After step 4, Explorer should initiate RPM request for Low Limit Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Low Limit property of Analog Input Object | 1.07.06-82 | 2025-02-27
67 | Read Property Multiple Service Initiation Support | TC_RPM_44 | Functional | To verify that, Software initiates RPM to read Dead Band property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Dead Band | 1. After step 4, Explorer should initiate RPM request for Dead Band Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Dead Band property of Analog Input Object | 1.07.06-82 | 2025-02-27
68 | Read Property Multiple Service Initiation Support | TC_RPM_45 | Functional | To verify that, Software initiates RPM to read Limit-Enable property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Limit-Enable | 1. After step 4, Explorer should initiate RPM request for limit-enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read limit-enable property of Analog Input Object | 1.07.06-82 | 2025-02-27
69 | Read Property Multiple Service Initiation Support | TC_RPM_46 | Functional | To verify that, Software initiates RPM to read Event-Enable property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Event-Enable | 1. After step 4, Explorer should initiate RPM request for Event-Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event-Enable property of Analog Input Object | 1.07.06-82 | 2025-02-27
70 | Read Property Multiple Service Initiation Support | TC_RPM_47 | Functional | To verify that, Software initiates RPM to read Acked Transition property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Acked Transition | 1. After step 4, Explorer should initiate RPM request for Acked Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Acked Transition property of Analog Input Object | 1.07.06-82 | 2025-02-27
71 | Read Property Multiple Service Initiation Support | TC_RPM_48 | Functional | To verify that, Software initiates RPM to read Notify Type property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Notify Type | 1. After step 4, Explorer should initiate RPM request for Notify Type Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notify Type property of Analog Input Object | 1.07.06-82 | 2025-02-27
72 | Read Property Multiple Service Initiation Support | TC_RPM_49 | Functional | To verify that, Software initiates RPM to read Event Time Stamp property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Event Time Stamp | 1. After step 4, Explorer should initiate RPM request for Event Time Stamp Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Time Stamp property of Analog Input Object | 1.07.06-82 | 2025-02-27
73 | Read Property Multiple Service Initiation Support | TC_RPM_50 | Functional | To verify that, Software initiates RPM to read Event Detection Enable property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Object Property :- Event Detection Enable | 1. After step 4, Explorer should initiate RPM request for Event Detection Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Detection Enable property of Analog Input Object | 1.07.06-82 | 2025-02-27
74 | Read Property Multiple Service Initiation Support | TC_RPM_51 | Functional | To verify that, Software initiates RPM to read Min-Pres-Value property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Min-Pres-Value | 1. After step 4, Explorer should initiate RPM request for Min-Pres-Value Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Min-Pres-Value property of Analog Output Object | 1.07.06-82 | 2025-02-27
75 | Read Property Multiple Service Initiation Support | TC_RPM_52 | Functional | To verify that, Software initiates RPM to read Max-Pres-Value property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Max-Pres-Value | 1. After step 4, Explorer should initiate RPM request for Max-Pres-Value Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Max-Pres-Value property of Analog Output Object | 1.07.06-82 | 2025-02-27
76 | Read Property Multiple Service Initiation Support | TC_RPM_53 | Functional | To verify that, Software initiates RPM to read Cov Increment property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Cov Increment | 1. After step 4, Explorer should initiate RPM request for Cov Increment Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Cov Increment property of Analog Output Object | 1.07.06-82 | 2025-02-27
77 | Read Property Multiple Service Initiation Support | TC_RPM_54 | Functional | To verify that, Software initiates RPM to read Priority Array property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Priority Array | 1. After step 4, Explorer should initiate RPM request for Priority Array Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Priority Array property of Analog Output Object | 1.07.06-82 | 2025-02-27
78 | Read Property Multiple Service Initiation Support | TC_RPM_55 | Functional | To verify that, Software initiates RPM to read Time-Delay property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Time-Delay | 1. After step 4, Explorer should initiate RPM request for Time-Delay Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Time-Delay property of Analog Output Object | 1.07.06-82 | 2025-02-27
79 | Read Property Multiple Service Initiation Support | TC_RPM_56 | Functional | To verify that, Software initiates RPM to read Notification-Class property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Notification-Class | 1. After step 4, Explorer should initiate RPM request for Notification-Class Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notification-Class property of Analog Output Object | 1.07.06-82 | 2025-02-27
80 | Read Property Multiple Service Initiation Support | TC_RPM_57 | Functional | To verify that, Software initiates RPM to read High Limit property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- High Limit | 1. After step 4, Explorer should initiate RPM request for High Limit Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read High Limit property of Analog Output Object | 1.07.06-82 | 2025-02-27
81 | Read Property Multiple Service Initiation Support | TC_RPM_58 | Functional | To verify that, Software initiates RPM to read Low Limit property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Low Limit | 1. After step 4, Explorer should initiate RPM request for Low Limit Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Low Limit property of Analog Output Object | 1.07.06-82 | 2025-02-27
82 | Read Property Multiple Service Initiation Support | TC_RPM_59 | Functional | To verify that, Software initiates RPM to read Dead Band property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Dead Band | 1. After step 4, Explorer should initiate RPM request for Dead Band Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Dead Band property of Analog Output Object | 1.07.06-82 | 2025-02-27
83 | Read Property Multiple Service Initiation Support | TC_RPM_60 | Functional | To verify that, Software initiates RPM to read Limit-Enable property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Limit-Enable | 1. After step 4, Explorer should initiate RPM request for Limit-Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Limit-Enable property of Analog Output Object | 1.07.06-82 | 2025-02-27
84 | Read Property Multiple Service Initiation Support | TC_RPM_61 | Functional | To verify that, Software initiates RPM to read Event-Enable property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Event-Enable | 1. After step 4, Explorer should initiate RPM request for Event-Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event-Enable property of Analog Output Object | 1.07.06-82 | 2025-02-27
85 | Read Property Multiple Service Initiation Support | TC_RPM_62 | Functional | To verify that, Software initiates RPM to read Acked-Transition property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Acked-Transition | 1. After step 4, Explorer should initiate RPM request for Acked-Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Acked-Transition property of Analog Output Object | 1.07.06-82 | 2025-02-27
86 | Read Property Multiple Service Initiation Support | TC_RPM_63 | Functional | To verify that, Software initiates RPM to read Notify-Type property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :-Notify-Type | 1. After step 4, Explorer should initiate RPM request for Acked-Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notify-Type property of Analog Output Object | 1.07.06-82 | 2025-02-27
87 | Read Property Multiple Service Initiation Support | TC_RPM_64 | Functional | To verify that, Software initiates RPM to read Event-Time-Stamp property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Object Property :- Event-Time-Stamp | 1. After step 4, Explorer should initiate RPM request for Event-Time-Stamp Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event-Time-Stamp property of Analog Output Object | 1.07.06-82 | 2025-02-27
88 | Read Property Multiple Service Initiation Support | TC_RPM_65 | Functional | To verify that, Software initiates RPM to read Date-List property of Calendar Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Calendar Object Property :- Date-List | 1. After step 4, Explorer should initiate RPM request for date-List Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Date-List property of Calendar Object | 1.07.06-82 | 2025-02-27
89 | Read Property Multiple Service Initiation Support | TC_RPM_66 | Functional | To verify that, Software initiates RPM to read File-Access-Method property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :- File-Access-Method | 1. After step 4, Explorer should initiate RPM request for File-Access-Method Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read File-Access-Method property of File Object | 1.07.06-82 | 2025-02-27
90 | Read Property Multiple Service Initiation Support | TC_RPM_67 | Functional | To verify that, Software initiates RPM to read Read only property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :- Read only | 1. After step 4, Explorer should initiate RPM request for Read only Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Read only property of File Object | 1.07.06-82 | 2025-02-27
91 | Read Property Multiple Service Initiation Support | TC_RPM_68 | Functional | To verify that, Software initiates RPM to read Archive property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :- Archive | 1. After step 4, Explorer should initiate RPM request for Archive Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Archive property of File Object | 1.07.06-82 | 2025-02-27
92 | Read Property Multiple Service Initiation Support | TC_RPM_69 | Functional | To verify that, Software initiates RPM to read Modification-date property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :- Modification-date | 1. After step 4, Explorer should initiate RPM request for Modification-date Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Modification-date property of File Object | 1.07.06-82 | 2025-02-27
93 | Read Property Multiple Service Initiation Support | TC_RPM_70 | Functional | To verify that, Software initiates RPM to read File-Type property of File Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: File Object Property :- File-Type | 1. After step 4, Explorer should initiate RPM request for File-Type Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read File-Type property of File Object | 1.07.06-82 | 2025-02-27
94 | Read Property Multiple Service Initiation Support | TC_RPM_71 | Functional | To verify that, Software initiates RPM to read Acked Transition property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Acked Transition | 1. After step 4, Explorer should initiate RPM request for Acked Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Acked Transition property of Binary Input Object | 1.07.06-82 | 2025-02-28
95 | Read Property Multiple Service Initiation Support | TC_RPM_72 | Functional | To verify that, Software initiates RPM to read Active Text property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :-Active Text | 1. After step 4, Explorer should initiate RPM request for Active Text Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Active Text property of Binary Input Object | 1.07.06-82 | 2025-02-28
96 | Read Property Multiple Service Initiation Support | TC_RPM_73 | Functional | To verify that, Software initiates RPM to read Alarm Values property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :-Alarm Values | 1. After step 4, Explorer should initiate RPM request for Alarm Values Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Alarm Values property of Binary Input Object | 1.07.06-82 | 2025-02-28
97 | Read Property Multiple Service Initiation Support | TC_RPM_74 | Functional | To verify that, Software initiates RPM to read Elapsed Active Time property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Elapsed Active Time | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Elapsed Active Time property of Binary Input Object | 1.07.06-82 | 2025-02-28
98 | Read Property Multiple Service Initiation Support | TC_RPM_75 | Functional | To verify that, Software initiates RPM to read Event Detection Enable property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Event Detection Enable | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Detection Enable property of Binary Input Object | 1.07.06-82 | 2025-02-28
99 | Read Property Multiple Service Initiation Support | TC_RPM_76 | Functional | To verify that, Software initiates RPM to read Event Enable property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Event Enable | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Enable property of Binary Input Object | 1.07.06-82 | 2025-02-28
100 | Read Property Multiple Service Initiation Support | TC_RPM_77 | Functional | To verify that, Software initiates RPM to read Inactive Text property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Inactive Text | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Inactive Text property of Binary Input Object | 1.07.06-82 | 2025-02-28
101 | Read Property Multiple Service Initiation Support | TC_RPM_78 | Functional | To verify that, Software initiates RPM to read Notification Class property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Notification Class | 1. After step 4, Explorer should initiate RPM request for Notification Class Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notification Class property of Binary Input Object | 1.07.06-82 | 2025-02-28
102 | Read Property Multiple Service Initiation Support | TC_RPM_79 | Functional | To verify that, Software initiates RPM to read Notify Type property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Notify Type | 1. After step 4, Explorer should initiate RPM request for Notify Type Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notify Type property of Binary Input Object | 1.07.06-82 | 2025-02-28
103 | Read Property Multiple Service Initiation Support | TC_RPM_80 | Functional | To verify that, Software initiates RPM to read Polarity property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Polarity | 1. After step 4, Explorer should initiate RPM request for Polarity Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Polarity property of Binary Input Object | 1.07.06-82 | 2025-02-28
104 | Read Property Multiple Service Initiation Support | TC_RPM_81 | Functional | To verify that, Software initiates RPM to read Time Delay property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Time Delay | 1. After step 4, Explorer should initiate RPM request for Polarity Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Time Delay property of Binary Input Object | 1.07.06-82 | 2025-02-28
105 | Read Property Multiple Service Initiation Support | TC_RPM_82 | Functional | To verify that, Software initiates RPM to read Time Delay property of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property :- Time Delay | 1. After step 4, Explorer should initiate RPM request for Polarity Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Time Delay property of Binary Input Object | 1.07.06-82 | 2025-02-28
106 | Read Property Multiple Service Initiation Support | TC_RPM_83 | Functional | To verify that, Software initiates RPM to read Acked Transition property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Acked Transition | 1. After step 4, Explorer should initiate RPM request for Acked Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Acked Transition property of Binary output Object | 1.07.06-82 | 2025-02-28
107 | Read Property Multiple Service Initiation Support | TC_RPM_84 | Functional | To verify that, Software initiates RPM to read Active Text property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Active Text | 1. After step 4, Explorer should initiate RPM request for Active Text Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Active Text property of Binary output Object | 1.07.06-82 | 2025-02-28
108 | Read Property Multiple Service Initiation Support | TC_RPM_85 | Functional | To verify that, Software initiates RPM to read Elapsed Active Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Elapsed Active Time | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Elapsed Active Time property of Binary output Object | 1.07.06-82 | 2025-02-28
109 | Read Property Multiple Service Initiation Support | TC_RPM_86 | Functional | To verify that, Software initiates RPM to read Event Enable property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Event Enable | 1. After step 4, Explorer should initiate RPM request for Event Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Enable property of Binary output Object | 1.07.06-82 | 2025-02-28
110 | Read Property Multiple Service Initiation Support | TC_RPM_87 | Functional | To verify that, Software initiates RPM to read Inactive Text property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Inactive Text | 1. After step 4, Explorer should initiate RPM request for Inactive Text Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Inactive Text property of Binary output Object | 1.07.06-82 | 2025-02-28
111 | Read Property Multiple Service Initiation Support | TC_RPM_88 | Functional | To verify that, Software initiates RPM to read Minimum Off Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Minimum Off Time | 1. After step 4, Explorer should initiate RPM request for Minimum Off Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Minimum Off Time property of Binary output Object | 1.07.06-82 | 2025-02-28
112 | Read Property Multiple Service Initiation Support | TC_RPM_89 | Functional | To verify that, Software initiates RPM to read Minimum On Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Minimum On Time | 1. After step 4, Explorer should initiate RPM request for Minimum On Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Minimum On Time property of Binary output Object | 1.07.06-82 | 2025-02-28
113 | Read Property Multiple Service Initiation Support | TC_RPM_90 | Functional | To verify that, Software initiates RPM to read Notification Class property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Notification Class | 1. After step 4, Explorer should initiate RPM request for Notification Class Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notification Class property of Binary output Object | 1.07.06-82 | 2025-02-28
114 | Read Property Multiple Service Initiation Support | TC_RPM_91 | Functional | To verify that, Software initiates RPM to read Notify Type property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Notify Type | 1. After step 4, Explorer should initiate RPM request for Notify Type Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Notify Type property of Binary output Object | 1.07.06-82 | 2025-02-28
115 | Read Property Multiple Service Initiation Support | TC_RPM_92 | Functional | To verify that, Software initiates RPM to read Polarity property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Polarity | 1. After step 4, Explorer should initiate RPM request for Polarity Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Polarity property of Binary output Object | 1.07.06-82 | 2025-02-28
116 | Read Property Multiple Service Initiation Support | TC_RPM_93 | Functional | To verify that, Software initiates RPM to read Time Delay property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Time Delay | 1. After step 4, Explorer should initiate RPM request for Time Delay Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Polarity property of Binary output Object | 1.07.06-82 | 2025-02-28
117 | Read Property Multiple Service Initiation Support | TC_RPM_94 | Functional | To verify that, Software initiates RPM to read Acked Transition property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Acked Transition | 1. After step 4, Explorer should initiate RPM request for Acked Transition Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Acked Transition property of Binary output Object | 1.07.06-82 | 2025-02-28
118 | Read Property Multiple Service Initiation Support | TC_RPM_95 | Functional | To verify that, Software initiates RPM to read Active Text property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Active Text | 1. After step 4, Explorer should initiate RPM request for Active Text Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Active Text property of Binary output Object | 1.07.06-82 | 2025-02-28
119 | Read Property Multiple Service Initiation Support | TC_RPM_96 | Functional | To verify that, Software initiates RPM to read Alarm Values property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Alarm Values | 1. After step 4, Explorer should initiate RPM request for Alarm Values Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Alarm Values property of Binary output Object | 1.07.06-82 | 2025-02-28
120 | Read Property Multiple Service Initiation Support | TC_RPM_97 | Functional | To verify that, Software initiates RPM to read Change Of State Count property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Change Of State Count | 1. After step 4, Explorer should initiate RPM request for Change Of State Count Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Change Of State Count property of Binary output Object | 1.07.06-82 | 2025-02-28
121 | Read Property Multiple Service Initiation Support | TC_RPM_98 | Functional | To verify that, Software initiates RPM to read Change Of State Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Change Of State Time | 1. After step 4, Explorer should initiate RPM request for Change Of State Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Change Of State Time property of Binary output Object | 1.07.06-82 | 2025-02-28
122 | Read Property Multiple Service Initiation Support | TC_RPM_99 | Functional | To verify that, Software initiates RPM to read Elapsed Active Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Elapsed Active Time | 1. After step 4, Explorer should initiate RPM request for Elapsed Active Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Elapsed Active Time property of Binary output Object | 1.07.06-82 | 2025-02-28
123 | Read Property Multiple Service Initiation Support | TC_RPM_100 | Functional | To verify that, Software initiates RPM to read Event Detection Enable property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Event Detection Enable | 1. After step 4, Explorer should initiate RPM request for Event Detection Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Detection Enable property of Binary output Object | 1.07.06-82 | 2025-02-28
124 | Read Property Multiple Service Initiation Support | TC_RPM_101 | Functional | To verify that, Software initiates RPM to read Event Enable property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Event Enable | 1. After step 4, Explorer should initiate RPM request for Event Enable Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Enable property of Binary output Object | 1.07.06-82 | 2025-02-28
125 | Read Property Multiple Service Initiation Support | TC_RPM_102 | Functional | To verify that, Software initiates RPM to read Event Time Stamp property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Event Time Stamp | 1. After step 4, Explorer should initiate RPM request for Event Time Stamp Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Event Time Stamp property of Binary output Object | 1.07.06-82 | 2025-02-28
126 | Read Property Multiple Service Initiation Support | TC_RPM_103 | Functional | To verify that, Software initiates RPM to read Inactive Text property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Inactive Text | 1. After step 4, Explorer should initiate RPM request for Inactive Text Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Inactive Text property of Binary output Object | 1.07.06-82 | 2025-02-28
127 | Read Property Multiple Service Initiation Support | TC_RPM_104 | Functional | To verify that, Software initiates RPM to read Minimum Off Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Minimum Off Time | 1. After step 4, Explorer should initiate RPM request for Minimum Off Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Minimum Off Time property of Binary output Object | 1.07.06-82 | 2025-02-28
128 | Read Property Multiple Service Initiation Support | TC_RPM_105 | Functional | To verify that, Software initiates RPM to read Minimum On Time property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Minimum On Time | 1. After step 4, Explorer should initiate RPM request for Minimum On Time Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Minimum On Time property of Binary output Object | 1.07.06-82 | 2025-02-28
129 | Read Property Multiple Service Initiation Support | TC_RPM_106 | Functional | To verify that, Software initiates RPM to read Priority Array property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Priority Array | 1. After step 4, Explorer should initiate RPM request for Priority Array Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Priority Array property of Binary output Object | 1.07.06-82 | 2025-02-28
130 | Read Property Multiple Service Initiation Support | TC_RPM_107 | Functional | To verify that, Software initiates RPM to read Time Delay property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Time Delay | 1. After step 4, Explorer should initiate RPM request for Time Delay Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Time Delay property of Binary output Object | 1.07.06-82 | 2025-02-28
131 | Read Property Multiple Service Initiation Support | TC_RPM_108 | Functional | To verify that, Software initiates RPM to read Time Of Active Reset property of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 6. 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property :- Time Of Active Reset | 1. After step 4, Explorer should initiate RPM request for Time Of Active Reset Property 2. After step 4, Explorer should display the value received in Wireshark log. | Read Property Multiple service is initiated through Explorer to read Time Of Active Reset property of Binary output Object | 1.07.06-82 | 2025-02-28
132 | Write Property Service Initiation Support | TC_WP_08 | Functional | To verify that, Software initiates WP Service to Write Vendor Proprietary Value of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor proprietary value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Vendor Proprietary | 1. After step 4, Explorer should initiate WP request for Vendor Proprietary Value 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write vendor Proprietary Value property of Analog value Object | 1.07.06-82 | 2025-03-04
133 | Write Property Service Initiation Support | TC_WP_09 | Functional | To verify that, Software initiates WP Service to Write Cov Increment Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Cov Increment to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Cov Increment | 1. After step 4, Explorer should initiate WP request for Cov Increment 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Cov Increment property of Analog value Object | 1.07.06-82 | 2025-03-04
134 | Write Property Service Initiation Support | TC_WP_10 | Functional | To verify that, Software initiates WP Service to Write Time Delay Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Delay to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Time Delay | 1. After step 4, Explorer should initiate WP request for Time Delay 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Time Delay property of Analog value Object. | 1.07.06-82 | 2025-03-04
135 | Write Property Service Initiation Support | TC_WP_11 | Functional | To verify that, Software initiates WP Service to Write High limit of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on High Limit to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- High Limit | 1. After step 4, Explorer should initiate WP request for High Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write High Limit property of Analog value Object. | 1.07.06-82 | 2025-03-04
136 | Write Property Service Initiation Support | TC_WP_12 |  | To verify that, Software initiates WP Service to Write Priority Array of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Priority Array to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Priority Array | 1. After step 4, Explorer should initiate WP request for Priority Array 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Priority Array property of Analog value Object. | 1.07.06-82 | 2025-03-04
137 | Write Property Service Initiation Support | TC_WP_13 |  | To verify that, Software initiates WP Service to Write Low Limit of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Low Limit to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Low Limit | 1. After step 4, Explorer should initiate WP request for Low Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Low Limit property of Analog value Object. | 1.07.06-82 | 2025-03-04
138 | Write Property Service Initiation Support | TC_WP_14 |  | To verify that, Software initiates WP Service to Write Event Enable of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Event Enable | 1. After step 4, Explorer should initiate WP request for Event Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event Enable property of Analog value Object | 1.07.06-82 | 2025-03-04
139 | Write Property Service Initiation Support | TC_WP_15 |  | To verify that, Software initiates WP Service to Write Notify Type Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notify Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Notify Type | 1. After step 4, Explorer should initiate WP request for Notify Type 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notify Type property of Analog value Object | 1.07.06-82 | 2025-03-04
140 | Write Property Service Initiation Support | TC_WP_16 |  | To verify that, Software initiates WP Service to Write Limit Enable Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Limit Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Limit Enable | 1. After step 4, Explorer should initiate WP request for Limit Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Limit Enable property of Analog value Object | 1.07.06-82 | 2025-03-04
141 | Write Property Service Initiation Support | TC_WP_17 |  | To verify that, Software initiates WP Service to Write Deadband Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Deadband to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Deadband | 1. After step 4, Explorer should initiate WP request for Deadband 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Deadband property of Analog value Object | 1.07.06-82 | 2025-03-04
142 | Write Property Service Initiation Support | TC_WP_18 |  | To verify that, Software initiates WP Service to Write Notification Class Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notification Class property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Notification Class | 1. After step 4, Explorer should initiate WP request for Notification Class 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notification Class property of Analog value Object | 1.07.06-82 | 2025-03-04
143 | Write Property Service Initiation Support | TC_WP_20 |  | To verify that, Software initiates WP Service to Write Relinquish Default Property of Analog Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Relinquish Default property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog value Property :- Relinquish Default | 1. After step 4, Explorer should initiate WP request for Relinquish Default 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Relinquish Default property of Analog value Object | 1.07.06-82 | 2025-03-04
144 | Write Property Service Initiation Support | TC_WP_21 |  | To verify that, Software initiates WP Service to Write Event Detection Enable Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Detection Enable property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Event Detection Enable | 1. After step 4, Explorer should initiate WP request for Relinquish Default 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event Detection Enable property of Analog Input Object | 1.07.06-82 | 2025-03-04
145 | Write Property Service Initiation Support | TC_WP_22 |  | To verify that, Software initiates WP Service to Write Deadband Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Detection Enable property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Deadband | 1. After step 4, Explorer should initiate WP request for Deadband 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Deadband property of Analog Input Object | 1.07.06-82 | 2025-03-04
146 | Write Property Service Initiation Support | TC_WP_23 |  | To verify that, Software initiates WP Service to Write Event Enable Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Event Enable | 1. After step 4, Explorer should initiate WP request for Event Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event Enable property of Analog Input Object | 1.07.06-82 | 2025-03-04
147 | Write Property Service Initiation Support | TC_WP_24 |  | To verify that, Software initiates WP Service to Write Event State Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event State property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Event State | 1. After step 4, Explorer should initiate WP request for Event State 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event State property of Analog Input Object | 1.07.06-82 | 2025-03-04
148 | Write Property Service Initiation Support | TC_WP_25 |  | To verify that, Software initiates WP Service to Write High Limit Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on High Limit property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- High Limit | 1. After step 4, Explorer should initiate WP request for High Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write High Limit property of Analog Input Object | 1.07.06-82 | 2025-03-04
149 | Write Property Service Initiation Support | TC_WP_26 |  | To verify that, Software initiates WP Service to Write Limit Enable Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Limit Enable property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Limit Enable | 1. After step 4, Explorer should initiate WP request for Limit Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Limit Enable property of Analog Input Object | 1.07.06-82 | 2025-03-04
150 | Write Property Service Initiation Support | TC_WP_27 |  | To verify that, Software initiates WP Service to Write Low Limit Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Low Limit property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Low Limit | 1. After step 4, Explorer should initiate WP request for Low Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Low Limit property of Analog Input Object | 1.07.06-82 | 2025-03-04
151 | Write Property Service Initiation Support | TC_WP_28 |  | To verify that, Software initiates WP Service to Write Notification Class Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notification Class property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Notification Class | 1. After step 4, Explorer should initiate WP request for Notification Class 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notification Class property of Analog Input Object | 1.07.06-82 | 2025-03-04
152 | Write Property Service Initiation Support | TC_WP_29 |  | To verify that, Software initiates WP Service to Write Notify Type Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notify Type property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Notify Type | 1. After step 4, Explorer should initiate WP request for Notify Type 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notify Type property of Analog Input Object | 1.07.06-82 | 2025-03-04
153 | Write Property Service Initiation Support | TC_WP_30 |  | To verify that, Software initiates WP Service to Write Object Name Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Object Name | 1. After step 4, Explorer should initiate WP request for Object Name 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Object Name property of Analog Input Object | 1.07.06-82 | 2025-03-04
154 | Write Property Service Initiation Support | TC_WP_31 |  | To verify that, Software initiates WP Service to Write Out Of Service Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Out Of Service | 1. After step 4, Explorer should initiate WP request for Out Of Service 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Out Of Service property of Analog Input Object | 1.07.06-82 | 2025-03-04
155 | Write Property Service Initiation Support | TC_WP_32 |  | To verify that, Software initiates WP Service to Write Reliability Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Reliability | 1. After step 4, Explorer should initiate WP request for Reliability 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Reliability property of Analog Input Object | 1.07.06-82 | 2025-03-04
156 | Write Property Service Initiation Support | TC_WP_33 |  | To verify that, Software initiates WP Service to Write Time Delay Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Delay property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Time Delay | 1. After step 4, Explorer should initiate WP request for Time Delay 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Time Delay property of Analog Input Object | 1.07.06-82 | 2025-03-04
157 | Write Property Service Initiation Support | TC_WP_34 |  | To verify that, Software initiates WP Service to Write Units Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Units property to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- units | 1. After step 4, Explorer should initiate WP request for Units 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Units property of Analog Input Object | 1.07.06-82 | 2025-03-04
158 | Write Property Service Initiation Support | TC_WP_35 |  | To verify that, Software initiates WP Service to Write Vendor proprietary Property of Analog Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor Proprietary to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Input Property :- Vendor Proprietary | 1. After step 4, Explorer should initiate WP request for Vendor Proprietary 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Vendor Proprietary property of Analog Input Object | 1.07.06-82 | 2025-03-04
159 | Write Property Service Initiation Support | TC_WP_36 |  | To verify that, Software initiates WP Service to Write Cov Increment Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Cov Increment to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Cov Increment | 1. After step 4, Explorer should initiate WP request for Cov Increment 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Cov Increment property of Analog Output Object | 1.07.06-82 | 2025-03-04
160 | Write Property Service Initiation Support | TC_WP_37 |  | To verify that, Software initiates WP Service to Write current Command Priority Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Current Command priority to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Current Command Priority | 1. After step 4, Explorer should initiate WP request for Current Command priority 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Current Command Priority property of Analog Output Object | 1.07.06-82 | 2025-03-04
161 | Write Property Service Initiation Support | TC_WP_38 |  | To verify that, Software initiates WP Service to Write current Command Priority Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Current Command priority to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Current Command Priority | 1. After step 4, Explorer should initiate WP request for Current Command priority 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Current Command Priority property of Analog Output Object | 1.07.06-82 | 2025-03-04
162 | Write Property Service Initiation Support | TC_WP_39 |  | To verify that, Software initiates WP Service to Write Event Enable Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Event Enable | 1. After step 4, Explorer should initiate WP request for Event Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event Enable property of Analog Output Object | 1.07.06-82 | 2025-03-04
163 | Write Property Service Initiation Support | TC_WP_40 |  | To verify that, Software initiates WP Service to Write Event State Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event State to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Event State | 1. After step 4, Explorer should initiate WP request for Event State 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Event State property of Analog Output Object | 1.07.06-82 | 2025-03-04
164 | Write Property Service Initiation Support | TC_WP_41 |  | To verify that, Software initiates WP Service to Write High Limit Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on High Limit to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- High Limit | 1. After step 4, Explorer should initiate WP request for High Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write High Limit property of Analog Output Object | 1.07.06-82 | 2025-03-04
165 | Write Property Service Initiation Support | TC_WP_42 |  | To verify that, Software initiates WP Service to Write Limit Enable Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Limit Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Limit Enable | 1. After step 4, Explorer should initiate WP request for Limit Enable 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Limit Enable property of Analog Output Object | 1.07.06-82 | 2025-03-04
166 | Write Property Service Initiation Support | TC_WP_43 |  | To verify that, Software initiates WP Service to Write Low Limit Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Low Limit to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Low Limit | 1. After step 4, Explorer should initiate WP request for Low Limit 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Low Limit property of Analog Output Object | 1.07.06-82 | 2025-03-04
167 | Write Property Service Initiation Support | TC_WP_44 |  | To verify that, Software initiates WP Service to Write Max Pres Value Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Max Pres Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Max Pres value | 1. After step 4, Explorer should initiate WP request for Max Pres Value 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Max Pres Value property of Analog Output Object | 1.07.06-82 | 2025-03-04
168 | Write Property Service Initiation Support | TC_WP_45 |  | To verify that, Software initiates WP Service to Write Min Pres Value Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Min Pres Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Min Pres value | 1. After step 4, Explorer should initiate WP request for Min Pres Value 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Min Pres Value property of Analog Output Object | 1.07.06-82 | 2025-03-04
169 | Write Property Service Initiation Support | TC_WP_46 |  | To verify that, Software initiates WP Service to Write Notification Class Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notification Class to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Notification Class | 1. After step 4, Explorer should initiate WP request for Notification Class 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notification Class property of Analog Output Object | 1.07.06-82 | 2025-03-04
170 | Write Property Service Initiation Support | TC_WP_47 |  | To verify that, Software initiates WP Service to Write Notify Type Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notify Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Notify Type | 1. After step 4, Explorer should initiate WP request for Notify Type 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Notify Type property of Analog Output Object | 1.07.06-82 | 2025-03-04
171 | Write Property Service Initiation Support | TC_WP_48 |  | To verify that, Software initiates WP Service to Write Object Name Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Object Name | 1. After step 4, Explorer should initiate WP request for Object Name 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Object Name property of Analog Output Object | 1.07.06-82 | 2025-03-04
172 | Write Property Service Initiation Support | TC_WP_49 |  | To verify that, Software initiates WP Service to Write Out Of Service Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Out Of Service | 1. After step 4, Explorer should initiate WP request for Out Of Service 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Out Of service property of Analog Output Object | 1.07.06-82 | 2025-03-04
173 | Write Property Service Initiation Support | TC_WP_50 |  | To verify that, Software initiates WP Service to Write Present Value Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Present value | 1. After step 4, Explorer should initiate WP request for Present Value 2. After step 4, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Present Value property of Analog Output Object | 1.07.06-82 | 2025-03-04
174 | Write Property Service Initiation Support | TC_WP_51 |  | To verify that, Software initiates WP Service to Write Priority Array Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Priority Array to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Priority Array | 1. After step 4, Explorer should initiate WP request for Priority Array 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Priority Array property of Analog Output Object | 1.07.06-82 | 2025-03-04
175 | Write Property Service Initiation Support | TC_WP_52 |  | To verify that, Software initiates WP Service to Write Reliability Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Reliability | 1. After step 4, Explorer should initiate WP request for Reliability 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Reliability property of Analog Output Object | 1.07.06-82 | 2025-03-04
176 | Write Property Service Initiation Support | TC_WP_53 |  | To verify that, Software initiates WP Service to Write Relinquish Default Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Relinquish Default to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Relinquish Default | 1. After step 4, Explorer should initiate WP request for Relinquish Default 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Relinquish Default property of Analog Output Object | 1.07.06-82 | 2025-03-04
177 | Write Property Service Initiation Support | TC_WP_54 |  | To verify that, Software initiates WP Service to Write Vendor Proprietary Value of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor Proprietary Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Vendor Proprietary value | 1. After step 4, Explorer should initiate WP request for Vendor Proprietary value 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Vendor Proprietary Value of Analog Output Object | 1.07.06-82 | 2025-03-04
178 | Write Property Service Initiation Support | TC_WP_55 |  | To verify that, Software initiates WP Service to Write Time Delay of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time delay to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Time Delay | 1. After step 4, Explorer should initiate WP request for Time delay 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Time Delay of Analog Output Object | 1.07.06-82 | 2025-03-04
179 | Write Property Service Initiation Support | TC_WP_56 |  | To verify that, Software initiates WP Service to Write Units Property of Analog Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Units to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Analog Output Property :- Units | 1. After step 4, Explorer should initiate WP request for Units 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Units of Analog Output Object | 1.07.06-82 | 2025-03-04
180 | Write Property Service Initiation Support | TC_WP_57 |  | To verify that, Software initiates WP Service to Write Ack Required Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Ack Required to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property :- Ack Required | 1. After step 4, Explorer should initiate WP request for Ack required 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Ack Required of Notification Class | 1.07.06-82 | 2025-03-04
181 | Write Property Service Initiation Support | TC_WP_58 |  | To verify that, Software initiates WP Service to Write Object Name Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property :- Object Name | 1. After step 4, Explorer should initiate WP request for Object Name 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Object Name of Notification Class | 1.07.06-82 | 2025-03-04
182 | Write Property Service Initiation Support | TC_WP_59 |  | To verify that, Software initiates WP Service to Write Object Type Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property :- Object Type | 1. After step 4, Explorer should initiate WP request for Object Type 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to Write Object Type of Notification Class | 1.07.06-82 | 2025-03-04
183 | Write Property Service Initiation Support | TC_WP_60 |  | To verify that, Software initiates WP Service to Write Priority Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Priority to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property : Priority | 1. After step 4, Explorer should initiate WP request for Priority 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Priority of Notification Class | 1.07.06-82 | 2025-03-04
184 | Write Property Service Initiation Support | TC_WP_61 |  | To verify that, Software initiates WP Service to Write Profile Name Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Profile Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property : Profile Name | 1. After step 4, Explorer should initiate WP request for Profile Name 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Profile Name of Notification Class | 1.07.06-82 | 2025-03-04
185 | Write Property Service Initiation Support | TC_WP_62 |  | To verify that, Software initiates WP Service to Write Recipient List Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Recipient List to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property : Recipient List | 1. After step 4, Explorer should initiate WP request for Recipient List 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Recipient List of Notification Class | 1.07.06-82 | 2025-03-04
186 | Write Property Service Initiation Support | TC_WP_63 |  | To verify that, Software initiates WP Service to Write vendor Proprietary Value Property Notification Class | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor Proprietary Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Notification Class Property : Vendor Proprietary value | 1. After step 4, Explorer should initiate WP request for Vendor Proprietary Value 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Vendor Proprietary Value of Notification Class | 1.07.06-82 | 2025-03-04
187 | Write Property Service Initiation Support | TC_WP_64 |  | To verify that, Software initiates WP Service to Write Effective Period Property of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Effective Period to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Effective Period | 1. After step 4, Explorer should initiate WP request for Effective Period 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Effective Period of Schedule Object | 1.07.06-82 | 2025-03-04
188 | Write Property Service Initiation Support | TC_WP_65 |  | To verify that, Software initiates WP Service to Write Exception Schedule Property of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Exception Schedule to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Exception Schedule | 1. After step 4, Explorer should initiate WP request for Exception Schedule 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Exception Schedule of Schedule Object | 1.07.06-82 | 2025-03-04
189 | Write Property Service Initiation Support | TC_WP_66 |  | To verify that, Software initiates WP Service to Write List Of Object Property reference of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on List Of Object Property Reference to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : List Of Object Property Reference | 1. After step 4, Explorer should initiate WP request for List Of Object Property Reference 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write List Of Object Property Reference of Schedule Object | 1.07.06-82 | 2025-03-04
190 | Write Property Service Initiation Support | TC_WP_67 |  | To verify that, Software initiates WP Service to Write Object Name of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Object Name | 1. After step 4, Explorer should initiate WP request for Object Name 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Name of Schedule Object | 1.07.06-82 | 2025-03-04
191 | Write Property Service Initiation Support | TC_WP_68 |  | To verify that, Software initiates WP Service to Write Object Type of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Object Type | 1. After step 4, Explorer should initiate WP request for Object Type 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Type of Schedule Object | 1.07.06-82 | 2025-03-04
192 | Write Property Service Initiation Support | TC_WP_69 |  | To verify that, Software initiates WP Service to Write Out Of Service of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Out Of Service | 1. After step 4, Explorer should initiate WP request for Out Of Service 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Out Of Service of Schedule Object | 1.07.06-82 | 2025-03-04
193 | Write Property Service Initiation Support | TC_WP_70 |  | To verify that, Software initiates WP Service to Write Present value of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Present Value | 1. After step 4, Explorer should initiate WP request for Present Value 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Present Value of Schedule Object | 1.07.06-82 | 2025-03-04
194 | Write Property Service Initiation Support | TC_WP_71 |  | To verify that, Software initiates WP Service to Write Priority For Writing of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Priority For Writing to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Object Property : Priority For Writing | 1. After step 4, Explorer should initiate WP request for Priority For Writing 2. After step 5, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Priority For Writing of Schedule Object | 1.07.06-82 | 2025-03-04
195 | Read Range Service Initiation Support | TC_RR_01 |  | To verify that, Software initiates Read Range Service to Read Log Buffer property for Trend Log Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on Object(eg Trend Log) to be tested. 5. Explorer should initiate Read Range-Request for Log buffer Property 6. Explorer should display Records collected in Log Buffer | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Trend Log Property : Log Buffer | However, there is no special provision provide on Explorer to send Read Range-Request | Read Range service is not initiated through Explorer to Read Log Buffer of Trend Log Object | 1.07.06-82 | 2025-03-04
196 | Write Property Service Initiation Support | TC_WP_72 |  | To verify that, Software initiates WP Service to Write Profile Name For Writing of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Profile Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Property : Profile Name | 1. After step 5, Explorer should initiate WP request For Writing Profile Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Profile Name For Writing of Schedule Object | 1.07.06-82 | 2025-03-04
197 | Write Property Service Initiation Support | TC_WP_73 |  | To verify that, Software initiates WP Service to Write Relibity property of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Property : Reliability | 1. After step 5, Explorer should initiate WP request For Writing Reliability 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Reliability of Schedule Object | 1.07.06-82 | 2025-03-06
198 | Write Property Service Initiation Support | TC_WP_74 |  | To verify that, Software initiates WP Service to Write Weekly Schedule property of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Weekly Schedule to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Property : Weekly Schedule | 1. After step 5, Explorer should initiate WP request for Writing Weekly Schedule 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Weekly Schedule of Schedule Object | 1.07.06-82 | 2025-03-06
199 | Write Property Service Initiation Support | TC_WP_75 |  | To verify that, Software initiates WP Service to Write Vendor Proprietary Value of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor Proprietary Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Property : Vendor Proprietary | 1. After step 5, Explorer should initiate WP request for Vendor Proprietary Value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Vendor Proprietary Value of Schedule Object | 1.07.06-82 | 2025-03-06
200 | Write Property Service Initiation Support | TC_WP_76 |  | To verify that, Software initiates WP Service to Write Schedule Default of Schedule Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Schedule Default to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Schedule Property : Schedule Default | 1. After step 5, Explorer should initiate WP request for Schedule default 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Schedule Default of Schedule Object | 1.07.06-82 | 2025-03-06
201 | Write Property Service Initiation Support | TC_WP_77 |  | To verify that, Software initiates WP Service to Write Object Name of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Object Name | 1. After step 5, Explorer should initiate WP request for Object Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Name of Accumulator Object | 1.07.06-82 | 2025-03-06
202 | Write Property Service Initiation Support | TC_WP_78 |  | To verify that, Software initiates WP Service to Write Object Type of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Object Type | 1. After step 5, Explorer should initiate WP request for Object Type 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Type of Accumulator Object | 1.07.06-82 | 2025-03-06
203 | Write Property Service Initiation Support | TC_WP_79 |  | To verify that, Software initiates WP Service to Write Out Of Service of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Out Of Service | 1. After step 5, Explorer should initiate WP request for Out Of Service 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Out Of Service of Accumulator Object | 1.07.06-82 | 2025-03-06
204 | Write Property Service Initiation Support | TC_WP_80 |  | To verify that, Software initiates WP Service to Write Present Value of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Present value | 1. After step 5, Explorer should initiate WP request for Present Value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Present Value of Accumulator Object | 1.07.06-82 | 2025-03-06
205 | Write Property Service Initiation Support | TC_WP_81 |  | To verify that, Software initiates WP Service to Write Profile Name of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Profile Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Profile Name | 1. After step 5, Explorer should initiate WP request for Profile Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Profile Name of Accumulator Object | 1.07.06-82 | 2025-03-06
206 | Write Property Service Initiation Support | TC_WP_82 |  | To verify that, Software initiates WP Service to Write Reliability of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Reliability | 1. After step 5, Explorer should initiate WP request for Reliability 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Reliability of Accumulator Object | 1.07.06-82 | 2025-03-06
207 | Write Property Service Initiation Support | TC_WP_83 |  | To verify that, Software initiates WP Service to Write Units of Accumulator Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Units to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Accumulator Property : Units | 1. After step 5, Explorer should initiate WP request for units 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Units of Accumulator Object | 1.07.06-82 | 2025-03-06
208 | Write Property Service Initiation Support | TC_WP_84 |  | To verify that, Software initiates WP Service to Write Active Text of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Active Text to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Active Text | 1. After step 5, Explorer should initiate WP request for Active Text 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Active Text of Binary Input Object | 1.07.06-82 | 2025-03-06
209 | Write Property Service Initiation Support | TC_WP_85 |  | To verify that, Software initiates WP Service to Write Alarm values of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Alarm Values to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Alarm Values | 1. After step 5, Explorer should initiate WP request for Alarm Values 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Alarm Values of Binary Input Object | 1.07.06-82 | 2025-03-06
210 | Write Property Service Initiation Support | TC_WP_86 |  | To verify that, Software initiates WP Service to Write Change Of State Count of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Change Of State Count to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Change State Count | 1. After step 5, Explorer should initiate WP request for Change Of State Count 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Count of Binary Input Object | 1.07.06-82 | 2025-03-06
211 | Write Property Service Initiation Support | TC_WP_87 |  | To verify that, Software initiates WP Service to Write Change Of State Time of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Change Of State Time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Change State Time | 1. After step 5, Explorer should initiate WP request for Change Of State Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Time of Binary Input Object | 1.07.06-82 | 2025-03-06
212 | Write Property Service Initiation Support | TC_WP_88 |  | To verify that, Software initiates WP Service to Write Event Enable of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Event Enable | 1. After step 5, Explorer should initiate WP request for Event Enable 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event Enable of Binary Input Object | 1.07.06-82 | 2025-03-06
213 | Write Property Service Initiation Support | TC_WP_89 |  | To verify that, Software initiates WP Service to Write Event State of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event State to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Event State | 1. After step 5, Explorer should initiate WP request for Event State 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event State of Binary Input Object | 1.07.06-82 | 2025-03-06
214 | Write Property Service Initiation Support | TC_WP_90 |  | To verify that, Software initiates WP Service to Write Notification Class of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notification class to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Notification Class | 1. After step 5, Explorer should initiate WP request for Notification Class 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Notification Class of Binary Input Object | 1.07.06-82 | 2025-03-06
215 | Write Property Service Initiation Support | TC_WP_91 |  | To verify that, Software initiates WP Service to Write Notify Type of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notify Type class to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Notify Type | 1. After step 5, Explorer should initiate WP request for Notify Type 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Notify Type of Binary Input Object | 1.07.06-82 | 2025-03-06
216 | Write Property Service Initiation Support | TC_WP_92 |  | To verify that, Software initiates WP Service to Write Object Name of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name class to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Object Name | 1. After step 5, Explorer should initiate WP request for Object Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Name of Binary Input Object | 1.07.06-82 | 2025-03-06
217 | Write Property Service Initiation Support | TC_WP_93 |  | To verify that, Software initiates WP Service to Write Object Type of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Type class to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Object Type | 1. After step 5, Explorer should initiate WP request for Object Type 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Type of Binary Input Object | 1.07.06-82 | 2025-03-06
218 | Write Property Service Initiation Support | TC_WP_94 |  | To verify that, Software initiates WP Service to Write Out Of Service of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Out Of Service | 1. After step 5, Explorer should initiate WP request for Out Of Service 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Out Of Service of Binary Input Object | 1.07.06-82 | 2025-03-06
219 | Write Property Service Initiation Support | TC_WP_95 |  | To verify that, Software initiates WP Service to Write Polarity of Binary Input Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Polarity to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Input Property : Polarity | 1. After step 5, Explorer should initiate WP request for Polarity 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Polarity of Binary Input Object | 1.07.06-82 | 2025-03-06
220 | Register Foreign Device | TC_FD_01 |  | To Verify that, the initiates Register Foreign Request | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on setting 5. Go to configuration 6. Enable BBMD-System level 7. In enable BBMD enter BBMD IP Adress(192.168.1.104) 8. Apply the changes and go to Explorer 9. Verify that initiates Register Foreign Device request | 1. Software should be initialized. | Positive | Enable BBMD -System Level: 192.168.1.104 | 1. After step 7, Explorer should initiate Register Foreign Device request | successfully initiates Register Foreign Device request | 1.07.06-99 | 2025-03-07
221 | Polling Period | TC_PP_01 |  | To Verify that, the software starts the RPM after a designated polling period. | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on setting 5. Set the Polling period as required 6. Wait till the polling period ends 7. verify initiates RPM after specified Polling period | 1. Software should be initialized. | Positive | Polling Period = 5 seconds | 1. After step 6, Explorer should initiate RPM request after every 5 seconds | initiates RPM successfully after every 5 seconds | 1.07.06-99 | 2025-03-07
222 | Register Foreign Device | TC_FD_02 |  | To Verify that, the initiates Register Foreign Request after every 60 sec( Any value given in Time To Live Parameter) | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on setting 5. Go to configuration 6. Enable BBMD-System level 7. In enable BBMD enter BBMD IP Adress(192.168.1.104), Mentioned Time To Live Parameter(60 seconds) 8. Apply the changes and go to Explorer 9. Verify that initiates Register Foreign Device request | 1. Software should be initialized. | Positive | Enable BBMD -System Level: 192.168.1.104 Time To Live Parameter: 60 Seconds | 1. After step 7, Explorer should register itself as Foreign Device after every 60 seconds | successfully initiates Register Foreign Device request | 1.07.06-99 | 2025-03-07
223 | Register Foreign Device | TC_FD_03 |  | To Verify that after registering as Foreign Device, it should initiates Who Is ( Distribute Broadcast Network ) | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on setting 5. Go to configuration 6. Enable BBMD-System level 7. In enable BBMD enter BBMD IP Adress(192.168.1.104) 8. Apply the changes and go to Explorer 9.initiate Who is request from to BBMD network 10. Verify in Wireshark that initiate Distribute Broadcast to network | 1. Software should be initialized. | Positive | Enable BBMD -System Level: 192.168.1.104 Time To Live Parameter: 60 Seconds | 1. After step 9, should initiates Who Is ( Distribute Broadcast Network ) | successfully initiates Who Is ( Distribute Broadcast Network ) | 1.07.06-99 | 2025-03-07
224 | Write Property Service Initiation Support | TC_WP_96 |  | To verify that, Software initiates WP Service to Write Present Value of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Present Value | 1. After step 5, Explorer should initiate WP request for Present Value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Present Value of Binary Input Object | 1.07.06-82 | 2025-03-06
225 | Write Property Service Initiation Support | TC_WP_97 |  | To verify that, Software initiates WP Service to Write Profile Name of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Profile Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Profile Name | 1. After step 5, Explorer should initiate WP request for Profile Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Profile Name of Binary Value Object | 1.07.06-82 | 2025-03-06
226 | Write Property Service Initiation Support | TC_WP_98 |  | To verify that, Software initiates WP Service to Write Reliability of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Reliability | 1. After step 5, Explorer should initiate WP request for Reliability 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Reliability of Binary Value Object | 1.07.06-82 | 2025-03-06
227 | Write Property Service Initiation Support | TC_WP_99 |  | To verify that, Software initiates WP Service to Write Time Delay of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Delay to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Time Delay | 1. After step 5, Explorer should initiate WP request for Time Delay 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Delay of Binary Value Object | 1.07.06-82 | 2025-03-06
228 | Write Property Service Initiation Support | TC_WP_100 |  | To verify that, Software initiates WP Service to Write Time Of Active Time Reset of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Of Active Time Reset to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Time Of Active Time Reset | 1. After step 5, Explorer should initiate WP request for Time Of Active Time Reset 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Of Active Time Reset of Binary Value Object | 1.07.06-82 | 2025-03-06
229 | Write Property Service Initiation Support | TC_WP_101 |  | To verify that, Software initiates WP Service to Write Change Of State Count of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Change Of State Count to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Change Of State Count | 1. After step 5, Explorer should initiate WP request for Change Of State Count 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Count of Binary Value Object | 1.07.06-82 | 2025-03-06
230 | Write Property Service Initiation Support | TC_WP_102 |  | To verify that, Software initiates WP Service to Write Alarm Values of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Alarm Values to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Alarm Values | 1. After step 5, Explorer should initiate WP request for Alarm Values 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Alarm Values of Binary Value Object | 1.07.06-82 | 2025-03-06
231 | Write Property Service Initiation Support | TC_WP_103 |  | To verify that, Software initiates WP Service to Write Change Of State Time of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Change Of State time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Change Of State Time | 1. After step 5, Explorer should initiate WP request for Change Of State Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Time of Binary Value Object | 1.07.06-82 | 2025-03-06
232 | Write Property Service Initiation Support | TC_WP_104 |  | To verify that, Software initiates WP Service to Write Elapsed Active Time of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Elapsed Active Time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Elapsed Active Time | 1. After step 5, Explorer should initiate WP request for Elapsed Active Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Elapsed Active Time of Binary Value Object | 1.07.06-82 | 2025-03-06
233 | Write Property Service Initiation Support | TC_WP_105 |  | To verify that, Software initiates WP Service to Write Event Detection Enable of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Detection Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Event Detection Enable | 1. After step 5, Explorer should initiate WP request for Event Detection Enable 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event Detection Enable Time of Binary Value Object | 1.07.06-82 | 2025-03-06
234 | Write Property Service Initiation Support | TC_WP_106 |  | To verify that, Software initiates WP Service to Write Event Enable of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Event Enable | 1. After step 5, Explorer should initiate WP request for Event Enable 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event Enable Time of Binary Value Object | 1.07.06-82 | 2025-03-06
235 | Write Property Service Initiation Support | TC_WP_107 |  | To verify that, Software initiates WP Service to Write Event State of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event State to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Event State | 1. After step 5, Explorer should initiate WP request for Event State 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event State Time of Binary Value Object | 1.07.06-82 | 2025-03-06
236 | Write Property Service Initiation Support | TC_WP_108 |  | To verify that, Software initiates WP Service to Write Notify Type of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Notify Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Notify Type | 1. After step 5, Explorer should initiate WP request for Notify Type 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Notify Type of Binary Value Object | 1.07.06-82 | 2025-03-06
237 | Write Property Service Initiation Support | TC_WP_109 |  | To verify that, Software initiates WP Service to Write Out Of Service of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Out Of Service | 1. After step 5, Explorer should initiate WP request for Out Of Service 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Out Of service of Binary Value Object | 1.07.06-82 | 2025-03-06
238 | Write Property Service Initiation Support | TC_WP_110 |  | To verify that, Software initiates WP Service to Write Present Value of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Present Value | 1. After step 5, Explorer should initiate WP request for Present Value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Present value of Binary Value Object | 1.07.06-82 | 2025-03-06
239 | Write Property Service Initiation Support | TC_WP_111 |  | To verify that, Software initiates WP Service to Write Priority Array of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Priority Array to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Priority Array | 1. After step 5, Explorer should initiate WP request for Priority Array 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Priority Array of Binary Value Object | 1.07.06-82 | 2025-03-06
240 | Write Property Service Initiation Support | TC_WP_112 |  | To verify that, Software initiates WP Service to Write Relinquish Default of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Relinquish Default to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Relinquish Default | 1. After step 5, Explorer should initiate WP request for Relinquish Default 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Relinquish Default of Binary Value Object | 1.07.06-82 | 2025-03-06
241 | Write Property Service Initiation Support | TC_WP_113 |  | To verify that, Software initiates WP Service to Write Time Of Active Time Reset of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Of Active Time Rese to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Time Of Active Time Reset | 1. After step 5, Explorer should initiate WP request for Time Of Active Time Reset 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Of Active Time Reset of Binary Value Object | 1.07.06-82 | 2025-03-06
242 | Write Property Service Initiation Support | TC_WP_114 |  | To verify that, Software initiates WP Service to Write Vendor Proprietary Value of Binary Value Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Vendor Proprietary Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Value Property : Vendor Proprietary Value | 1. After step 5, Explorer should initiate WP request for Vendor Proprietary Value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Vendor Proprietary Value of Binary Value Object | 1.07.06-82 | 2025-03-06
243 | Write Property Service Initiation Support | TC_WP_115 |  | To verify that, Software initiates WP Service to Write Change Of State Time of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Change Of State Time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Change Of State Time | 1. After step 5, Explorer should initiate WP request for Change Of State Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Time of Binary output Object | 1.07.06-82 | 2025-03-06
244 | Write Property Service Initiation Support | TC_WP_116 |  | To verify that, Software initiates WP Service to Write Current Command Priority of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Current Command Priority to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Current Command Priority | 1. After step 5, Explorer should initiate WP request for Change Of State Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Change Of State Time of Binary Output Object | 1.07.06-82 | 2025-03-06
245 | Write Property Service Initiation Support | TC_WP_117 |  | To verify that, Software initiates WP Service to Write Event Detection Enable of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Detection Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Event detection Enable | 1. After step 5, Explorer should initiate WP request for Event Detection Enable 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event Detection Enable Time of Binary Output Object | 1.07.06-82 | 2025-03-06
246 | Write Property Service Initiation Support | TC_WP_118 |  | To verify that, Software initiates WP Service to Write Event State of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event State to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Event State | 1. After step 5, Explorer should initiate WP request for Event State 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event State of Binary Output Object | 1.07.06-82 | 2025-03-06
247 | Write Property Service Initiation Support | TC_WP_119 |  | To verify that, Software initiates WP Service to Write Event Enable of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Event Enable to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Event Enable | 1. After step 5, Explorer should initiate WP request for Event Enable 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Event Enable of Binary Output Object | 1.07.06-82 | 2025-03-06
248 | Write Property Service Initiation Support | TC_WP_120 |  | To verify that, Software initiates WP Service to Write feedback value of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on feedback Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Feedback value | 1. After step 5, Explorer should initiate WP request for feedback value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write feedback Value of Binary Output Object | 1.07.06-82 | 2025-03-06
249 | Write Property Service Initiation Support | TC_WP_121 |  | To verify that, Software initiates WP Service to Write Inactive text of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Inactive Text to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Inactive Text | 1. After step 5, Explorer should initiate WP request for Inactive Text 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Inactive Text of Binary Output Object | 1.07.06-82 | 2025-03-06
250 | Write Property Service Initiation Support | TC_WP_122 |  | To verify that, Software initiates WP Service to Write Minimum Off Time of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Minimum Off Time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Minimum Off Time | 1. After step 5, Explorer should initiate WP request for Minimum Off Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Minimum Off Time of Binary Output Object | 1.07.06-82 | 2025-03-06
251 | Write Property Service Initiation Support | TC_WP_123 |  | To verify that, Software initiates WP Service to Write Minimum On Time of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Minimum On Time to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Minimum On Time | 1. After step 5, Explorer should initiate WP request for Minimum On Time 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Minimum On Time of Binary Output Object | 1.07.06-82 | 2025-03-06
252 | Write Property Service Initiation Support | TC_WP_124 |  | To verify that, Software initiates WP Service to Write Object Name of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Object Name | 1. After step 5, Explorer should initiate WP request for Object Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Name of Binary Output Object | 1.07.06-82 | 2025-03-06
253 | Write Property Service Initiation Support | TC_WP_125 |  | To verify that, Software initiates WP Service to Write Object Type of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Object Type to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Object Type | 1. After step 5, Explorer should initiate WP request for Object Type 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Object Type of Binary Output Object | 1.07.06-82 | 2025-03-06
254 | Write Property Service Initiation Support | TC_WP_126 |  | To verify that, Software initiates WP Service to Write Out Of Service of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Out Of Service to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Out of service | 1. After step 5, Explorer should initiate WP request for Out Of Service 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Out Of Service of Binary Output Object | 1.07.06-82 | 2025-03-06
255 | Write Property Service Initiation Support | TC_WP_127 |  | To verify that, Software initiates WP Service to Write Polarity of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Polarity to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Polarity | 1. After step 5, Explorer should initiate WP request for Polarity 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Polarity of Binary Output Object | 1.07.06-82 | 2025-03-06
256 | Write Property Service Initiation Support | TC_WP_128 |  | To verify that, Software initiates WP Service to Write Present Value of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Present Value to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Present value | 1. After step 5, Explorer should initiate WP request for Present value 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Present value of Binary Output Object | 1.07.06-82 | 2025-03-06
257 | Write Property Service Initiation Support | TC_WP_129 |  | To verify that, Software initiates WP Service to Write Profile Name of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Profile Name to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Profile Name | 1. After step 5, Explorer should initiate WP request for Profile Name 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Profile Name of Binary Output Object | 1.07.06-82 | 2025-03-06
258 | Write Property Service Initiation Support | TC_WP_130 |  | To verify that, Software initiates WP Service to Write Reliability of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Reliability to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Reliability | 1. After step 5, Explorer should initiate WP request for Reliability 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Reliability of Binary Output Object | 1.07.06-82 | 2025-03-06
259 | Write Property Service Initiation Support | TC_WP_131 |  | To verify that, Software initiates WP Service to Write Relinquish Default of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Relinquish Default to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Relinquish Default | 1. After step 5, Explorer should initiate WP request for Relinquish Default 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Relinquish Default of Binary Output Object | 1.07.06-82 | 2025-03-06
260 | Write Property Service Initiation Support | TC_WP_132 |  | To verify that, Software initiates WP Service to Write Time Delay of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Delay to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Time Delay | 1. After step 5, Explorer should initiate WP request for Time Delay 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Delay of Binary Output Object | 1.07.06-82 | 2025-03-06
261 | Write Property Service Initiation Support | TC_WP_133 |  | To verify that, Software initiates WP Service to Write Time Of Active Reset of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Of Active Reset to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Time Of Active Reset | 1. After step 5, Explorer should initiate WP request for Time Of Active Reset 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Of Active reset of Binary Output Object | 1.07.06-82 | 2025-03-06
262 | Write Property Service Initiation Support | TC_WP_134 |  | To verify that, Software initiates WP Service to Write Time Of State Reset of Binary Output Object | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on any Object to be tested (eg BO Object) 5. Double click on Time Of State Reset to write 6. Enter after writing the value 5. Review response from TD | 1. Software should be initialized. | Positive | Refer test data from Objects tab Object: Binary Output Property : Time Of State Reset | 1. After step 5, Explorer should initiate WP request for Time Of State Reset 2. After step 6, Explorer should display the value received in Wireshark log. | Write Property service is initiated through Explorer to write Time Of State Reset of Binary Output Object | 1.07.06-82 | 2025-03-06
263 | Register Foreign Device | TC_FD_04 |  | To verify that Explorer(192.168.10.106) will initiate Read-Broadcast-DistributionTable NAK to every Read-Broadcast-Distribution-Table request send by BBMD device (192.168.11.107) | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Click on setting 5. Go to configuration 6. Enable BBMD-System level 7. In enable BBMD enter BBMD IP Adress(192.168.11.107) 8. Write BDT of Explorer from other BBMD device (192.168.11.107) 9. Read BDT of Explorer (192.168.10.106) from BBMD Device (192.168.11.107) 10. Verify in Wireshark that Explorer initiate Write-Broadcast-Distribution-Table NAK | 1. Software should be initialized. | Positive | Enable BBMD -System Level: 192.168.11.107 Explorer: 192.168.10.107 Time To Live Parameter: 60 Seconds | 1. After step 9, BBMD Device (192.168.11.107) should initiate Read-Broadcast_Distribution-Table request in response Explorer(192.168.10.107)should respond with Read-Broadcast-Distribution-Table NAK | Explorer successfully responded with Read-Broadcast-Distribution-Table NAK to BBMD Device. | 1.07.06-99 | 2025-03-10
264 | Register Foreign Device | TC_FD_05 |  | To verify the UI representation of when there are two BBMD devices in different subnets and Register FD is sent to any one of the BBMD devices | 1. Initialize Software. 2. Click on explorer menu. 3. Click on setting 4. Go to configuration 5. Enable BBMD-System level 6. In enable BBMD enter BBMD IP Adress(192.168.0.104) also configured Time to Live Parameter for 60 Seconds. 7. Make IUT to initiate Register Foreign Device to BBMD(192.168.0.104) 8. Received successful completion for Register Foreign Device Request 9. Make IUT(192.168.10.106) to initiate Who Is request to BBMD(192.168.0.104) 10. verify the request in Wireshark log | 1. Software should be initialized. | Positive | Enable BBMD -System Level: 192.168.0.104 Time To Live Parameter: 60 Seconds | 1. After step 7, Explorer should initiate Register Foreign Device to BBMD and BBMD should respond with successful completion Also verify the Discovery tree on User interface | successfully initiated Register FD request and discovered on explorer | 1.07.06-99 | 2025-03-10
265 | User Interface | TC_UI_01 | Functional | Verify the Functioning of the "Setting" | 1. Initialize Software. 2. Click on explorer menu. 3. Click on Setting 4. Window will Pop up of Explorer Setting 4. verify the properties present under Setting i.e. 1. Auto Discovery on startup 2. Who is Wait Time 3. write Priority(1-16) 4. Poll Properties | 1. Software should be initialized. | Positive |  | After Step4, All the Properties in "Setting" should be Displayed as Shown in Screenshot | All the properties present on Explorer>Setting is Displayed and functional | 1.07.06-110 | 2025-03-11
266 | User Interface | TC_UI_02 | Functional | Verify that devices are discovered on the Network and are accessible | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Verify the Devices are discovered on the network | 1. Software should be initialized. | Positive |  | After Step4, devices should be discovered on the Network and accessible from the Explorer | devices are discovered on the Network successfully and are accessible through Explorer | 1.07.06-110 | 2025-03-11
267 | User Interface | TC_UI_03 | Functional | Verify the Rapid Polling of any Object/Properties | 1. Initialize Software. 2. Click on explorer menu. 3. Click on Setting 4. Configure Short Polling Period from polling properties 5. Click on the TD Discovered in explorer 6. Select one objects/properties to poll simultaneously 7. Verify that Explorer automatically reinitiate RPM/RP request after every 15 seconds | 1. Software should be initialized. | Positive | Once it initiates with all RPM/RP request then at last it initiated with Property List property and again after 15 seconds it will start to initiates RPM/RP request. Polling Period = 15 seconds Object = Binary Value | After Step6, Explorer Should automatically reinitiate RPM/RP request after the specified polling period | Successfully initiated Rapid Polling of any Object/Properties | 1.07.06-110 | 2025-03-11
268 | User Interface | TC_UI_04 | Functional | Verify the reconnection after a transient Network Drop | 1. Initialize Software. 2. Click on explorer. 3. Click on TD discovered in explorer. 4. Disconnect the Network of Explorer 5. Add another device to network when TD is already discovered in network 6.Restore the Network of Explorer 7. TD should get displayed on Explorer and also in background on Wireshark, Explorer should start reading the properties of both the devices | 1. Software should be initialized. | Positive |  | After Step6, explorer should automatically discovered in network and start reading the properties of both the devices on Wireshark log | Both the Devices were successfully discovered on Explorer and in background it started reading the properties of both the devices. | 1.07.06-110 | 2025-03-13
269 | User Interface | TC_UI_05 | Functional | Verify the Test Device reconnection after a power cycle | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Turn off Device or power cycle the Device 5. After Power cycle once the Device is ON, Verify Wireshark Logs. Explorers should read the properties of TD in Wireshark | 1. Software should be initialized. | Positive |  | After Step4, After power cycle of TD it should get discovered on Explorer and start read reading the properties in Wireshark | Explorer Successfully discovered the TD after power cycle of TD and started reading the properties device | 1.07.06-110 | 2025-03-11
270 | User Interface | TC_UI_06 | Functional | Verify error handling when device is unreachable | 1. Initialize Software. 2. Click on explorer menu. 3. Click on TD discovered in explorer. 4. Disconnect the Device and try to access it | 1. Software should be initialized. | Positive |  | After Step4, Appropriate error should pop up when device is disconnected | After Disconnecting device and tried to access it through explorer it successfully displayed the appropriate error (Error Code 21) | 1.07.06-110 | 2025-03-11
271 | User Interface | TC_UI_07 | Functional | Verify the Functioning of the "Refresh" | 1. Initialize Software. 2. Click on explorer menu. 3. Click on Refresh Button 4. verify the Refresh function also observe the behaviour in Wireshark log after refresh button is clicked | 1. Software should be initialized. | Positive |  | After Step4, that Explorer should get refreshed and initiate Who is | Refresh button correctly function and initiated Who is request successfully | 1.07.06-110 | 2025-03-12
272 | User Interface | TC_UI_08 | Functional | Verify the Functioning of the "IP Address" | 1. Initialize Software. 2.click on setting 3.click on config 4. configured the IP Adress 5. Click on explorer menu. 6. Verify that the IP Adress of should be present in IP Adress tab | 1. Software should be initialized. | Positive | IP Address: 192.168.10.106 | After Step3, In IP Address tab the IP should be present | In Explorer, IP Address is not present in IP Address tab | 1.07.06-110 | 2025-03-12
273 | User Interface | TC_UI_09 | Functional | Verify the Functioning of the "Port" | 1. Initialize Software. 2.click on setting 3.click on config 4. configured the Port 5. Click on explorer menu. 6. Verify that the Port of should be present in Port tab | 1. Software should be initialized. | Positive | Port: 47808 | After Step4, In Port tab it should correctly displayed as configured on Explorer | In Explorer, Port is not present in port tab | 1.07.06-110 | 2025-03-12
274 | User Interface | TC_UI_10 | Functional | Verify the Functioning of Number of Retries | 1. Initialize Software. 2. Click on Explorer > config>Retry Setting - Number of Retries i.e. 4 3. Verify that will send the confirm request to device | 1. Software should be initialized. | Positive | Number of Retries: 4 | After Step3, After setting the configuration, should attempt to communicate with the specified device. It should send a confirm request to the device. This can be verified by checking the device’s response or by monitoring the communication logs in to ensure the request was transmitted successfully. If the device doesn't respond, the retry mechanism should trigger up to 4 retries as per the configured setting | Explorer successfully attempted retry mechanism triggered up to 4 retries | 1.07.06-110 | 2025-03-13
275 | User Interface | TC_UI_11 | Functional | Verify that IP devices are discovered on the Network under Network: Local IP Device 102 IP Device 106 | 1. Initialize Software. 2. Click on explorer menu. 3. Click on IP Devices discovered on explorer. 4. Verify the Devices are discovered on the network and are accessible | 1. Software should be initialized. | Positive | Network: Local IP Device 102 IP Device 106 | After Step3, All the IP device should be discovered under Network: Local Also, all the devices are accessible through Explorer | Explorer successfully discovered IP devices with correct discovery under Network Local | 1.07.06-110 | 2025-03-12
276 | User Interface | TC_UI_12 | Functional | Verify that MSTP devices are discovered on the Network under Network: 4 PIC6DEMO 1610101 | 1. Initialize Software. 2. Click on explorer menu. 3. Click on MSTP Devices discovered on explorer. 4. Verify the Devices are discovered on the network and are accessible | 1. Software should be initialized. | Positive | Network: 4 PIC6DEMO 1610101 | After Step3, All the MSTP device should be discovered under Network: Local Also, all the devies are accessible through Explorer | Explorer successfully discovered MSTP devices with correct discovery under the Network: 4 | 1.07.06-110 | 2025-03-12